Seasonal Challenges for a Zero-Carbon Grid

1st Given Name Surname, 2nd Given Name Surname, and William R. Cherry (List authors on this line using 12 point Times font – use a second line if necessary)

Institute Name, City, State/Region, Mail/Zip Code, Country (authors’ affiliation(s) listed here in 12 point Times font – use a second line if necessary)

Abstract—Today resource adequacy is most often maintained by installing natural gas plants to meet the peak load. In California, the current risk of inadequate resource adequacy is highest around sunset in late summer. In a low-carbon grid, resource adequacy will increasingly require adequate stored energy or expanded complementarity through resource diversity throughout the entire year. Here we seek to develop an intuition about the times of the year when resource adequacy may be most challenged. We use a straightforward approach and show that the month of the biggest challenge may shift depending on the amount of solar and storage that are built.

Keywords—storage, zero-carbon grid

# Introduction

California has established a target of 2045 (SB100) for moving to a grid that delivers electricity reliably without carbon dioxide emissions, and many experts belie this target will be moved forward in time as we move further into the climate emergency. Meeting this target will require changes in resource adequacy planning. This challenge was highlighted in August 2020 when the California Independent System Operator (CAISO) declared an emergency and initiated rolling black outs on two days during a widespread heat wave. This was the first time in about 30 years that the state initiated rolling black outs because of the reserve margin dropping below safe levels. A root cause analysis showed that the problem arose from the extreme heat (and breadth of the heat wave) and inadequate planning targets for early evening hours. Several practices in the energy markets exacerbated the supply challenges.[1]

A simple consideration of a similar situation for a grid without natural gas plants shows that storage will need to supply most of the load after sundown on a windless evening. Thus, CAISO will need on the order of 40 GW (more, if the load increases) and adequate storage to run through the night. It is less obvious whether California will still be most susceptible to resource inadequacy during late August and early September or whether that risk will shift to other times of year.

It is anticipated that CAISO’s future zero-carbon grid will be dominated by solar generation.[2] While wind and other renewable electricity will supplement solar, the wind resource in California is highly variable and is even less reliable than solar resource in the winter. Monthly summer solar resource is about twice the winter solar resource in California, while the monthly load varies less, suggesting that winter may be the more challenging season for a zero-carbon grid in California.

This paper uses historical data to estimate the storage needed for a zero-carbon grid to understand when resource adequacy may be most difficult in California. We explore the effects of building more solar on the stored energy as well as on the amount of storage needed. We also explore the effect of limiting the rate of charge. Finally, we discuss the intuition that is gained from the results toward understanding how these factors affect the time of year when resource adequacy may be most challenging.

# Methodology

- The energy storage that will be needed to operate a zero-carbon grid in California was studied using historical CAISO electrical generation and load data [3]. These datasets include 5-min data for electrical generation by technology and for the electrical load. To simulate the grid of the future, the thermal, imports, and nuclear data were replaced with added solar generation. A hypothetical storage reservoir was created for balancing supply and demand. For each time point, the electricity available for charging the storage was calculated from equation 1.

| - Charge= Solar+Wind+Hydro+other renewables-Load | - (1) |
| --- | --- |

- where Solar was the scaled up solar generation and the other terms in equation 1 were taken directly from the historical data [3]. When the right side of equation 1 was positive, the state-of-charge of the hypothetical storage was increased and when it was negative, the stored energy was discharged into the grid. To simplify the analysis, battery charging and discharging efficiencies were assumed to be 100% and the minimum state of charge to be zero, neglecting the need for an operating reserve margin. When the solar generation was increased to supply more electricity than needed to meet the annual load, the size of the storage reservoir was capped. When the state-of-charge of the reservoir reached the cap, additional electricity available for charging was documented as surplus electricity. In practice, this electricity might be used for hydrogen production or some other load. For  this study, to gain intuition about when the system may face resource adequacy issues, we tracked the state-of-charge as a function of time of year and documented the size of reservoir needed and the surplus electricity generated as we varied the amount of solar electricity generated.

- For a subset of the calculations, the charging rate was limited to 40 GW and the extra power beyond this limit was considered to be surplus.

- This approach gave realistic results in that the generation and load profiles were based on observed data. However, this approach does not 1) consider transmission constraints, 2) adjust hydro generation to best meet the supply/demand imbalances, nor 3) adjust the load profile, which could be driven by EV adoption, demand management and many other things.

We could add:

## Trade-offs between expanded land-based generation of electricity and H2 vs. off-shore resource integration.

Fig.  1. Calculated state of charge for stored energy using 2019 generation and load data adjusted to reflect zero-carbon grid scenarios with variable solar. Each curve reflects a different annual solar-generation-to-load ratio (see legend). The charging rate was capped at 40 GW for all except for the 2 dotted lines.

July 25th 2019

July 1st, 2019

Fig.  2. Calculated state of charge for stored energy as in Fig. 1, but for six different years with the solar build selected to always supply 15 TWh of surplus.

This work was supported by the California Energy Commission.

# Results and Discussion

The state-of-charge of the storage as a function of time of year is shown in Fig. 1 using generation and load data from 2019, but with the solar generation scaled up to be able to meet or exceed the total load for the year. For all curves we observe that the state of charge is a minimum sometime during the winter, but the time for the minimum shifts from mid-March when the total generation just meets the annual load to mid-January when a large solar build out is capable of exceeding the daily demand on sunny days. A close look at the data (not shown) confirms that the minimum state of charge occurs near sunrise. Thus, the most challenging time of year to retain adequate reserve shifts from sunset in late summer (observed today) to sunrise in the winter (when storage is required to get through the winter months).

This calculation for 2019 is compared with similar data for years 2015-2020 in Fig. 2. We selected calculations with fairly similar solar build outs for all six years by adjusting the amount of solar so that the total electricity generated in each year exceeded the total load for that same year by 15 TWh. In every year, the minimum state-of-charge for the energy reservoir is found to occur in late February or the first part of March, narrowing the time of low reserve margin to about one month. The predictability of the most challenging month is consistent with the current predictability of late August and early September as the most challenging for today’s grid.

The upper part of Fig. 2 shows that the reservoir is not able to always recharge every day during the summer. The dips in the state-of-charge when the reservoir is mostly full come at different times each year. These could be caused by heat waves or by times of low solar generation. Our investigations showed that the cause was dominated by low solar generation, which was associated with clouds or smoke as shown in the two satellite images [4] of California shown for a day when the reservoir was able to completely refill (July 1, 2019) and a day when the reservoir was not able to refill completely (July 25, 2019), showing the obvious cloud cover. The year 2020 was notable because of the large number of fires that burned late in the summer, corresponding to an early decline in the state-of-charge of the hypothetical battery in 2020, as shown in Fig. 2, green curve. Despite the abnormally large amount of smoke in late summer of 2020, the year ended with a state-of-charge that was comparable to 2018.

Although smoke during the summer could be worrisome, Fig. 2 shows that a storage reservoir that is adequate for the winter will always be adequate during the summer, suggesting that our current concern for resource adequacy in late summer may disappear at some time in the future.

A number of studies have suggested that it will be beneficial to be able to charge the storage quickly when the sun is shining using a charge rate that is greater than the largest discharge rate. [5] Our comparison of unconstrained charging rates with charging rates limited to 40 GW (the common maximum discharge rate) is shown in Fig. 1. Limiting the charging rate delays the date when the reservoir reaches full charge, but has very little effect on the top (black) curve otherwise. The effect becomes greater when the solar fleet is built out more, enabling faster charging. For the red (bottommost) curve, unconstrained charging allows the reservoir to be completely filled one month earlier. It also decreases the size of the reservoir needed from about 7.3 to 6 TWh. The decrease in the size of the needed storage is significant, highlighting the benefit of being able to charge faster in a solar-rich grid.  We anticipate that the benefit of the higher charging rates will be more apparent in situations when the storage is being filled behind the meter by a local solar plant rather than from the grid with no transmission constraints.

The size of the storage needed as a function of the solar build out is shown in Fig. 3. For 2019, these data can be taken from Fig. 1. For the other years, the data were assembled in a similar manner. Only 3 of the six years are shown for clarity.

Fig.  3. Decrease of storage needed to meet minimal resource adequacy for greater solar buildout (left axis) and associated surplus electricity (right axis). The thick and thin lines differentiate the storage needed when the storage is allowed to charge at an unlimited rate or at a maximum of 40 GW, respectively.

Table I. Calculated storage reservoir size in energy and associated duration assuming 40 GW of storage

| Situation | Energy | Duration |
| --- | --- | --- |
| One night | 400 GWh | 10 h |
| Seasonal worst year low solar | 20 TWh | 500 h |
| Seasonal best year low solar | 16 TWh | 400 h |
| Seasonal worst year high solar | 8 TWh | 200 h |
| Seasonal best year high solar | 4 TWh | 100 h |

As expected, the size of storage reservoir needed decreases with increased solar investment. In general, the size of the storage that is needed decreases a factor of two or more for the range of solar investigated here (see Table I). The storage needed to get through the night is about a factor of 10 less than the seasonal storage needed, even with large solar investment (solar providing enough electricity to supply 125% of the load) and favorable weather. If the investment in solar energy is minimized, the required seasonal storage may be 50 times that needed to get through a single night.

As the needed storage decreases with added solar investment, the surplus electricity (dashed lines in Fig. 3) increases linearly with the amount of solar. This surplus electricity may be curtailed, but, more likely, it will be used to meet some other load. For example, the surplus electricity could be used to make fertilizer during the summer. The final paper will evaluate the practicality of using this intermittent electricity.

# Conclusions

The time with the greatest challenge to maintain adequate reserve margin for California’s grid may shift from late summer today to winter or spring for a solar-driven, zero-carbon grid. If the solar investment delivers about 80% of the electricity needed to meet load in a year, the tightest reserve margin may fall in March by using 40 GW of storage that could deliver that power for 500 h. If the solar fleet is built about 50% bigger, the tightest reserve may occur in January and require a storage reservoir that is less than half the size. Limiting the rate of charging to 40 GW increases the amount of storage needed slightly but has a bigger effect on the time during which the storage reservoir is close to being depleted. Thus, our intuition about resource adequacy for a zero-carbon grid will be informed by the solar investment as well as the design of the storage. Cloudy, smokey days during the summer may cause a depletion of energy in the storage reservoir, but will not lead to tight reserve margins during the summer – a major change from today’s picture. We note that these conclusions would not apply to locations that have a strong wind resource during the winter.

In the conference presentation we will also discuss the effects of inefficiency of dis/charging and other modifiers to the calculations.

##### References

[1]	http://www.caiso.com/Documents/Final-Root-Cause-Analysis-Mid-August-2020-Extreme-Heat-Wave.pdf

[2]	The solar resource in California is more consistent than the wind.

[3]	http://www.caiso.com/informed/Pages/ManagingOversupply.aspx

[4]	https://worldview.earthdata.nasa.gov

[5]	https://www.strategen.com/strategen-blog/long-duration-energy-storage-for-californias-clean-reliable-grid